Tera Term Instructions:

1. Download Tera Term from http://hp.vector.co.jp/authors/VA002416/ttermp23.zip

2. Unzip and run the setup.

3. Connect the PC to J11 connector of your ICPRO. The connection may be either RS232 or RS485 as long as the 2 jumpers above J11 are set 
according to your choice. In case you choose RS485, make sure the communication chip is installed in the socket above J11.

4. Run Tera Term, select Serial COM and set the COM no. according to the one used on your PC for the connection.

5. Go to Setup > Serial Port and set the baud rate to 115200

6. Reset the power to the ICPRO. The screen should display these lines:

  MEGA ANALYSER  Bank:45 Version:02/10/09 Type:23 Checksum:8ED692
Xn            : Crystal Multipliser by n (n=1,2 or 4)
XC            : Display CONGG1 TO CONFG4
Xaaaaaa[,nn]  : Display nn Ext./Flash Mem. Bytes from Addr.aaaaaa
Xaaaaaa=dd,.. : Write dd.. in Ext.Mem. from Addr.aaaaaa
Daa[,nn]      : Display nn Int.Mem. Bytes from Addr.aa
Daa=dd,..     : Write dd.. in Int.Mem. from Addr.aa
T=HHMMDDMMYYd : Set Time&Date
T             : Read Time&Date
O             : Read E2ROM
FEff[,ll]     : Flash Erase sectors ff(00-34) [to ll(00-34)]
Faaaaaa=dd    : Write dd in Flash Mem. Byte Addr.aaaaaa
FV            : Application and Boot Version
FLB           : Load Boot (Bank 5Fh) and Jump to Boot
FLA           : Load Application (Bank 45h/4Ah) Jump to Boot
FLnn          : Load File in Bank nn (45-5F)
Gaaaaaa       : Go from Address aaaaaa
?             : Display Commands List

M>

7. Type FV [Ent]. The ICPRO should show 3 lines, where the current firmware version is shown at either one of the first 2 lines. 
The other line (i.e., either the second or the first) would show 6 question marks ??/??/??. 
In this example the firmware version is 02/10/09. 

M>FV
??
 Bank:45 Version:02/10/09 Type:23 Checksum:8ED692
 Bank:4A Version:??/??/?? Type:?? Checksum:DF1E02
 Bank:5F Version:28/09/07 Type:FB Checksum:F28F01

M>

8. Type FLA [Ent]. The ICPRO would then ask for a file. 

M>FLA
PLEASE, SEND FILE

9. Go to File > Send File, and select the required HEX with the new firmware. Click OK to send the file. 
The Tera Term would send the file in few seconds.

10. To make sure the new firmware was sent correctly type FV [Ent] again and verify that the new date appears.

11. Exit Tera Term.